## Modbus Address Values
9.2 Data Protocols |  |  |  | Easygen 2500 Modbus address list
9.2.1 CANopen/Modbus
9.2.1.1 Data Protocol 5100 (Basic Visualization)
Modbus |  | CAN
Modicon start addr. | Start addr. (*1) | Data byte 0 (Mux) | Data byte | Parameter ID | Description | Multiplier | Units | Inactive Value-Gen1 | Inacive Value-Gen2 | Active Value-Gen1 | Active Value-Gen2
450001 | 450000 | 0 | 1,2 |  | Protocoll-ID, allways 5100 |  | -- | 5100 | 5100 |  | 5100
450002 | 450001 | 0 | 3,4 | 10100 | Pickup speed | 1 | rpm | 0 | 0 |  | 1501
450003 | 450002 | 0 | 5,6 | - | Control mode (STOP/AUTO/MANUAL) 1=AUTO 2=STOP 4=MANUAL | Mask:000Fh | (enu m.) | 3601 | 3601 |  | 3601
450004 | 450003 | 1 | 1,2 | 160 | Gen. Power factor | 0.001 |  | 1000 | 1000 |  | 975
450005 | 450004 | 1 | 3,4,5,6 | 170 | Av. Gen. Wye-Voltage | 0.1 | V | 0 | 0 |  | 0
450007 | 450006 | 2 | 1,2 | 144 | Gen. frequency | 0.01 | Hz | 0 | 0 |  | 5002
450008 | 450007 | 2 | 3,4,5,6 | 171 | Av. Gen. Delta-Voltage | 0.1 | V | 0 | 0 |  | 0
450010 | 450009 | 3 | 1,2 | 147 | Mains / Busbar frequency | 0.01 | Hz | 0 | 0 |  | 5002
450011 | 450010 | 3 | 3,4,5,6 | 173 | Av. Mains / Busbar Wye-Voltage | 0.1 | V | 0 | 0 |  | 0
450013 | 450012 | 4 | 1,2 | 208 | Mains / Busbar power factor | 0.001 |  | 1000 | 1000 |  | 1000
450014 | 450013 | 4 | 3,4,5,6 | 174 | Av. Mains / Busbar Delta-Voltage | 0.1 | V | 0 | 0 |  | 0
450016 | 450015 | 5 | 1,2 | 2540 | Engine, number of start requests | 1 |  | 115 | 78 |  | 79
450017 | 450016 | 5 | 3,4,5,6 | 135 | Total gen. power | 1 | W | 0 | 0 |  | 2
450019 | 450018 | 6 | 1,2 | 10202 | Operation modes |  | (enu m.) | 13253 | 13253 |  | 13251
13200 = Auxiliary services postrun
13216 = Idle run active
13201 = Aux. services prerun
13250 = Gen. stable time
13202 = Critical mode
13251 = In operation
13203 = Motor Stop
13252 = Power limited prerun
13204 = Cool down
13253 = AUTO mode ready
13205 = Mains settling
13254 = Ramp to rated
13206 = Engine Start
13255 = GCB open
13207 = Start - Pause
13256 = Unloading generator
13208 = Preglow
13257 = MCB open
13209 = GCB dead bus close
13258 = Loading generator
13210 = MCB dead bus close
13259 = Synchronization GCB
13211 = Emergency run
13260 = Synchronization MCB
13212 = Turning
13261 = GCB -> MCB Delay
13213 = Ignition
13262 = MCB -> GCB Delay
13214 = Crank protect
13263 = Start w/o Load
13215 = Emergency/Critical
13264 = Unloading mains
13281 = Derating active
13265 = Synchronization permissive
13266 = Synchronization check
13267 = Synchronization off
450020 | 450019 | 6 | 3,4,5,6 | 140 | Total mains power | 1 | W | 0 |  |  | 0
450022 | 450021 | 7 | 1,2 | 10110 | Battery voltage | 0.1 | V | 271 | 270 |  | 281
450023 | 450022 | 7 | 3,4,5,6 | 207 | Av. Mains Current | 0.001 | A | 0 | 0 |  | 0
450025 | 450024 | 8 | 1,2 | 10111 | Analog input 1 | changeable |  | 32767 | 32767 |  | 32767
450026 | 450025 | 8 | 3,4,5,6 | 185 | Av. Gen. Current | 0.001 | A | 0 | 0 |  | 4
450028 | 450027 | 9 | 1,2 | 10112 | Analog input 2 | changeable |  | 32767 | 32767 |  | 32767
450029 | 450028 | 9 | 3,4,5,6 | 161 | Meas. ground current | 0.001 | A | 0 | 0 |  | 0
450031 | 450030 | 10 | 1,2 | 10115 | Analog input 3 | changeable |  | 32767 | 32767 |  | 32767
450032 | 450031 | 10 | 3,4,5,6 | 159 | Calculated ground current | 0.001 | A | 0 | 0 |  | 0
450034 | 450033 | 11 | 1,2 | 4153 | Idle mode active (suppresses undervolt, underfreq,...) | Mask: 8000h | Bit | 1024 | 1024 |  | 2536
[5 empty] | Idle mode active | Mask: 4000h | Bit
[5 empty] | Start without closing GCB | Mask: 2000h | Bit
[5 empty] | internal | Mask: 1000h | Bit
[5 empty] | internal | Mask: 0800h | Bit
[5 empty] | internal | Mask: 0400h | Bit
[5 empty] | Cooldown is active | Mask: 0200h | Bit
[5 empty] | Auxiliary services generally active | Mask: 0100h | Bit
[5 empty] | Engine Monitoring delay timer has expired | Mask: 0080h | Bit
[5 empty] | Breaker delay timer has expired | Mask: 0040h | Bit
[5 empty] | Engine start is requested | Mask: 0020h | Bit
[5 empty] | Critical mode is active in automatic mode | Mask: 0010h | Bit
[5 empty] | Engine is released (speed governor is enabled) | Mask: 0008h | Bit
[5 empty] | Auxiliary services prerun is active | Mask: 0004h | Bit
[5 empty] | Auxiliary services postrun is active | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450035 | 450034 | 11 | 3,4,5,6 | 111 | Gen. current 1 | 0.001 | A | 0 | 0 |  | 4
450037 | 450036 | 12 | 1,2 | 4154 | Crank (Starter) is active | Mask: 8000h | Bit | 4096 | 4096 |  | 20480
[5 empty] | Operating Magnet / Gasrelay is active | Mask: 4000h | Bit
[5 empty] | Preglow / Ignition is active | Mask: 2000h | Bit
[5 empty] | Mains settling timer is running | Mask: 1000h | Bit
[5 empty] | Emergency mode is currently active | Mask: 0800h | Bit
[5 empty] | internal | Mask: 0400h | Bit
[5 empty] | internal | Mask: 0200h | Bit
[5 empty] | internal | Mask: 0100h | Bit
[5 empty] | internal | Mask: 0080h | Bit
[5 empty] | internal | Mask: 0040h | Bit
[5 empty] | Stopping Magnet is active | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0010h | Bit
[5 empty] | The genset runs mains parallel | Mask: 0008h | Bit
[5 empty] | internal | Mask: 0004h | Bit
[5 empty] | internal | Mask: 0002h | Bit
[5 empty] | Increment Engine Start Counter | Mask: 0001h | Bit
450038 | 450037 | 12 | 3,4,5,6 | 112 | Gen. current 2 | 0.001 | A | 0 | 0 |  | 3
450040 | 450039 | 13 | 1,2 | 4155 | 3-Position Controller Freq./Power raise | Mask: 8000h | Bit | 512 | 512 |  | 2048
[5 empty] | 3-Position Controller Freq./Power lower | Mask: 4000h | Bit
[5 empty] | 3-Position Controller Volt./ReactPow raise | Mask: 2000h | Bit
[5 empty] | 3-Position Controller Volt./ReactPow lower | Mask: 1000h | Bit
[5 empty] | GCB is closed | Mask: 0800h | Bit
[5 empty] | MCB is closed | Mask: 0400h | Bit
[5 empty] | internal | Mask: 0200h | Bit
[5 empty] | Synchronization GCB is active | Mask: 0100h | Bit
[5 empty] | Opening GCB is active | Mask: 0080h | Bit
[5 empty] | Closing GCB is active | Mask: 0040h | Bit
[5 empty] | Synchronization MCB is active | Mask: 0020h | Bit
[5 empty] | Opening MCB is active | Mask: 0010h | Bit
[5 empty] | Closing MCB is active | Mask: 0008h | Bit
[5 empty] | Unloading generator is active | Mask: 0004h | Bit
[5 empty] | Unloading mains is active | Mask: 0002h | Bit
[5 empty] | Power limited prerun | Mask: 0001h | Bit
450041 | 450040 | 13 | 3,4,5,6 | 113 | Gen. current 3 | 0.001 | A | 0 | 0 |  | 4
450043 | 450042 | 14 | 1,2 | 4156 | internal | Mask: 8000h | Bit | 0 | 0 |  | 900
[5 empty] | internal | Mask: 4000h | Bit
[5 empty] | internal | Mask: 2000h | Bit
[5 empty] | internal | Mask: 1000h | Bit
[5 empty] | internal | Mask: 0800h | Bit
[5 empty] | Dead busbar closure request for GCB or MCB | Mask: 0400h | Bit
[5 empty] | Active power load share is acitve | Mask: 0200h | Bit
[5 empty] | Reactive power load share is acitve | Mask: 0100h | Bit
[5 empty] | Generator with a closed GCB is requested | Mask: 0080h | Bit
[5 empty] | LDSS: The Engine is started | Mask: 0040h | Bit
[5 empty] | LDSS: The Engine is stopped | Mask: 0020h | Bit
[5 empty] | LDSS: The Engine is stopped, if possible | Mask: 0010h | Bit
[5 empty] | LDSS: Minimum Running Time is active | Mask: 0008h | Bit
[5 empty] | LDSS: The LDSS function is active | Mask: 0004h | Bit
[5 empty] | The Critical Mode Postrun is active | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450044 | 450043 | 14 | 3,4,5,6 | 134 | Mains current L1 | 0.001 | A | 0 | 0 |  | 0
450046 | 450045 | 15 | 1,2 | 10131 | internal | Mask: 0040h | Bit | 0 | 0 |  | 64
[5 empty] | Alarm class F latched | Mask: 0020h | Bit
[5 empty] | Alarm class E latched | Mask: 0010h | Bit
[5 empty] | Alarm class D latched | Mask: 0008h | Bit
[5 empty] | Alarm class C latched | Mask: 0004h | Bit
[5 empty] | Alarm class B latched | Mask: 0002h | Bit
[5 empty] | Alarm class A latched | Mask: 0001h | Bit
450047 | 450046 | 15 | 3,4,5,6 | 136 | Total gen. reactive power | 1 | var | 0 | 0 |  | 0
450049 | 450048 | 16 | 1,2 | 10310 | Analog output 1 | 0.01 | % | 4340 | 4340 |  | 5061
450050 | 450049 | 16 | 3,4,5,6 | 150 | Total mains reactive power | 1 | var | 0 | 0 |  | 0
450052 | 450051 | 17 | 1,2 | 10311 | Analog output 2 | 0.01 | % | 4999 | 4999 |  | 4907
450053 | 450052 | 17 | 3,4,5,6 | 108 | Gen. voltage L1-L2 | 0.1 | V | 0 | 0 |  | 0
450055 | 450054 | 18 | 1,2 | 10317 | Analog output 3 | 0.01 | % | 0 | 0 |  | 9986
450056 | 450055 | 18 | 3,4,5,6 | 114 | Gen. voltage L1-N | 0.1 | V | 0 | 0 |  | 0
450058 | 450057 | 19 | 1,2 | 10318 | Analog output 4 | 0.01 | % | 0 | 0 |  | 9986
450059 | 450058 | 19 | 3,4,5,6 | 109 | Gen. voltage L2-L3 | 0.1 | V | 0 | 0 |  | 0
450061 | 450060 | 20 | 1,2 | 10159 | AI Auxiliary excitation D+ | 0.1 | V | 0 | 0 |  | 284
450062 | 450061 | 20 | 3,4,5,6 | 115 | Gen. voltage L2-N | 0.1 | V | 0 | 0 |  | 0
450064 | 450063 | 21 | 1,2 | 2112 | Overspeed 1 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 2113 | Overspeed 2 latched | Mask: 4000h | Bit
|  |  |  | 2162 | Underspeed 1 latched | Mask: 2000h | Bit
|  |  |  | 2163 | Underspeed 2 latched | Mask: 1000h | Bit
|  |  |  | 2652 | Unintended stop latched | Mask: 0800h | Bit
|  |  |  | 2457 | Speed/freq.mism. Latched | Mask: 0400h | Bit
|  |  |  | 2504 | Shutdwn malfunct. latched | Mask: 0200h | Bit
|  |  |  | 2603 | GCB fail to close latched | Mask: 0100h | Bit
|  |  |  | 2604 | GCB fail to open latched | Mask: 0080h | Bit
|  |  |  | 2623 | MCB fail to close latched | Mask: 0040h | Bit
|  |  |  | 2624 | MCB fail to open latched | Mask: 0020h | Bit
|  |  |  | 10017 | CAN-Fault J1939 latched | Mask: 0010h | Bit
|  |  |  | 3325 | Start fail latched | Mask: 0008h | Bit
|  |  |  | 2560 | Mainten. days exceeded latched | Mask: 0004h | Bit
|  |  |  | 2561 | Mainten. hours exceeded latched | Mask: 0002h | Bit
|  |  |  | 10087 | CANopen error at CAN Interface 1 | Mask: 0001h | Bit
450065 | 450064 | 21 | 3,4,5,6 | 110 | Gen. voltage L3-L1 | 0.1 | V | 0 | 0 |  | 0
450067 | 450066 | 22 | 1,2 | 3064 | GCB syn. timeout latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 3074 | MCB syn. timeout latched | Mask: 4000h | Bit
[5 empty] | internal | Mask: 2000h | Bit
|  |  |  | 4056 | Charge alt. low voltage (D+) latched | Mask: 1000h | Bit
|  |  |  | 2944 | Ph.rotation mismatch latched | Mask: 0800h | Bit
[5 empty] | internal | Mask: 0400h
[5 empty] | internal | Mask: 0200h
[5 empty] | internal | Mask: 0100h
[5 empty] | internal | Mask: 0080h
[5 empty] | internal | Mask: 0040h
|  |  |  | 10088 | CANopen error at CAN Interface 2 | Mask: 0020h | Bit
|  |  |  | 4073 | Parameter Alignment | Mask: 0010h
|  |  |  | 4064 | Missing members on CAN | Mask: 0008h | Bit
|  |  |  | 1714 | EEPROM failure latched | Mask: 0004h | Bit
|  |  |  | 15125 | Red stop lamp latched | Mask: 0002h | Bit
|  |  |  | 15126 | Amber warning lamp latched | Mask: 0001h | Bit
450068 | 450067 | 22 | 3,4,5,6 | 116 | Gen. voltage L3-N | 0.1 | V | 0 | 0 |  | 0
450070 | 450069 | 23 | 1,2 | 2558 | Hours until next maintenance | 1 | h | 293 | 297 |  | 297
450071 | 450070 | 23 | 3,4,5,6 | 118 | Mains / Busbar voltage L1-L2 | 0.1 | V | 0 | 0 |  | 0
450073 | 450072 | 24 | 1,2 | 1912 | Gen.overfreq. 1 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 1913 | Gen.overfreq. 2 latched | Mask: 4000h | Bit
|  |  |  | 1962 | Gen.underfreq. 1 latched | Mask: 2000h | Bit
|  |  |  | 1963 | Gen.underfreq. 2 latched | Mask: 1000h | Bit
|  |  |  | 2012 | Gen.overvolt. 1 latched | Mask: 0800h | Bit
|  |  |  | 2013 | Gen.overvolt. 2 latched | Mask: 0400h | Bit
|  |  |  | 2062 | Gen.undervolt. 1 latched | Mask: 0200h | Bit
|  |  |  | 2063 | Gen.undervolt. 2 latched | Mask: 0100h | Bit
|  |  |  | 2218 | Gen. overcurr. 1 latched | Mask: 0080h | Bit
|  |  |  | 2219 | Gen. overcurr. 2 latched | Mask: 0040h | Bit
|  |  |  | 2220 | Gen. overcurr. 3 latched | Mask: 0020h | Bit
|  |  |  | 2262 | Gen. Rv/Rd pow.1 latched | Mask: 0010h | Bit
|  |  |  | 2263 | Gen. Rv/Rd pow.2 latched | Mask: 0008h | Bit
|  |  |  | 2314 | Gen. Overload IOP 1 latched | Mask: 0004h | Bit
|  |  |  | 2315 | Gen. Overload IOP 2 latched | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450074 | 450073 | 24 | 3,4,5,6 | 121 | Mains / Busbar voltage L1-N | 0.1 | V | 0 | 0 |  | 0
450076 | 450075 | 25 | 1,2 | 2412 | Unbal. load 1 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 2413 | Unbal. load 2 latched | Mask: 4000h | Bit
|  |  |  | 3907 | Gen. Asymmetry latched | Mask: 2000h | Bit
|  |  |  | 3263 | Ground fault 1 latched | Mask: 1000h | Bit
|  |  |  | 3264 | Ground fault 2 latched | Mask: 0800h | Bit
|  |  |  | 3955 | Gen. phase rot. misw. Latched | Mask: 0400h | Bit
|  |  |  | 2924 | Gen act.pwr mismatch Latched | Mask: 0200h | Bit
|  |  |  | 3124 | Gen. unloading fault Latched | Mask: 0100h | Bit
|  |  |  | 4038 | Inv.time ov.curr. Latched | Mask: 0080h | Bit
|  |  |  | 2664 | Operating range failed, latched | Mask: 0040h | Bit
|  |  |  | 2362 | Gen. Overload MOP 1 latched | Mask: 0020h | Bit
|  |  |  | 2363 | Gen. Overload MOP 2 latched | Mask: 0010h | Bit
|  |  |  | 2337 | Gen. overexcited 1 latched | Mask: 0008h | Bit
|  |  |  | 2338 | Gen. overexcited 2 latched | Mask: 0004h | Bit
|  |  |  | 2387 | Gen. underexcited 1 latched | Mask: 0002h | Bit
|  |  |  | 2388 | Gen. underexcited 2 latched | Mask: 0001h | Bit
450077 | 450076 | 25 | 3,4,5,6 | 119 | Mains / Busbar voltage L2-L3 | 0.1 | V | 0 | 0 |  | 0
450079 | 450078 | 26 | 1,2 | 2862 | Mains / Busbar ov.freq. 1 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 2863 | Mains / Busbar ov.freq. 2 latched | Mask: 4000h | Bit
|  |  |  | 2912 | Mains / Busbar un.freq. 1 latched | Mask: 2000h | Bit
|  |  |  | 2913 | Mains / Busbar un.freq. 2 latched | Mask: 1000h | Bit
|  |  |  | 2962 | Mains / Busbar ov.volt. 1 latched | Mask: 0800h | Bit
|  |  |  | 2963 | Mains / Busbar ov.volt. 2 latched | Mask: 0400h | Bit
|  |  |  | 3012 | Mains / Busbar un.volt. 1 latched | Mask: 0200h | Bit
|  |  |  | 3013 | Mains / Busbar un.volt. 2 latched | Mask: 0100h | Bit
|  |  |  | 3057 | Mains / Busbar phaseshift latched | Mask: 0080h | Bit
|  |  |  | 3114 | Mains / Busbar decoupling latched | Mask: 0040h | Bit
[5 empty] | internal | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0010h | Bit
[5 empty] | internal | Mask: 0008h | Bit
|  |  |  | 3975 | Mains phase rot. Miswired latched | Mask: 0004h | Bit
[5 empty] | internal | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450080 | 450079 | 26 | 3,4,5,6 | 122 | Mains / Busbar voltage L2-N | 0.1 | V | 0 | 0 |  | 0
450082 | 450081 | 27 | 1,2 |  | internal | Mask: 8000h | Bit | 0 | 0 |  | 0
[5 empty] | internal | Mask: 4000h | Bit
[5 empty] | internal | Mask: 2000h | Bit
[5 empty] | internal | Mask: 1000h | Bit
[5 empty] | internal | Mask: 0800h | Bit
[5 empty] | internal | Mask: 0400h | Bit
[5 empty] | internal | Mask: 0200h | Bit
[5 empty] | internal | Mask: 0100h | Bit
|  |  |  | 3106 | Mains df/dt | Mask: 0080h | Bit
|  |  |  | 2934 | Mns act.pwr mismatch latched | Mask: 0040h | Bit
|  |  |  | 4958 | Mns. Time-dep. Volt. | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0010h | Bit
|  |  |  | 8834 | Mns. Volt increase | Mask: 0008h | Bit
[5 empty] | internal | Mask: 0004h | Bit
|  |  |  | 3288 | QV monitoring 1 | Mask: 0002h | Bit
|  |  |  | 3289 | QV monitoring 2 | Mask: 0001h | Bit
450083 | 450082 | 27 | 3,4,5,6 | 120 | Mains / Busbar voltage L3-L1 | 0.1 | V | 0 | 0 |  | 0
450085 | 450084 | 28 | 1,2 | 10608 | State Digital Input 8 latched | Mask: 8000h | Bit | 0 | 0 |  | 512
|  |  |  | 10607 | State Digital Input 7 latched | Mask: 4000h | Bit
|  |  |  | 10605 | State Digital Input 6 latched | Mask: 2000h | Bit
|  |  |  | 10604 | State Digital Input 5 latched | Mask: 1000h | Bit
|  |  |  | 10603 | State Digital Input 4 latched | Mask: 0800h | Bit
|  |  |  | 10602 | State Digital Input 3 latched | Mask: 0400h | Bit
|  |  |  | 10601 | State Digital Input 2 latched | Mask: 0200h | Bit
|  |  |  | 10600 | State Digital Input 1 latched | Mask: 0100h | Bit
[5 empty] | internal | Mask: 0080h | Bit
[5 empty] | internal | Mask: 0040h | Bit
[5 empty] | internal | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0010h | Bit
[5 empty] | internal | Mask: 0008h | Bit
[5 empty] | internal | Mask: 0004h | Bit
[5 empty] | internal | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450086 | 450085 | 28 | 3,4,5,6 | 123 | Mains / Busbar voltage L3-N | 0.1 | V | 0 | 0 |  | 0
450088 | 450087 | 29 | 1,2 | 10610 | State Digital Input 10 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 10609 | State Digital Input 9 latched | Mask: 4000h | Bit
[5 empty] | internal | Mask: 3FFFh
450089 | 450088 | 29 | 3,4,5,6 | 2520 | Gen. real energy | 0.01 | MWh | 0 | 0 |  | 0
450091 | 450090 | 30 | 1,2 | 16376 | State external Digital Input 16 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 16375 | State external Digital Input 15 latched | Mask: 4000h | Bit
|  |  |  | 16374 | State external Digital Input 14 latched | Mask: 2000h | Bit
|  |  |  | 16373 | State external Digital Input 13 latched | Mask: 1000h | Bit
|  |  |  | 16372 | State external Digital Input 12 latched | Mask: 0800h | Bit
|  |  |  | 16371 | State external Digital Input 11 latched | Mask: 0400h | Bit
|  |  |  | 16370 | State external Digital Input 10 latched | Mask: 0200h | Bit
|  |  |  | 16369 | State external Digital Input 9 latched | Mask: 0100h | Bit
|  |  |  | 16368 | State external Digital Input 8 latched | Mask: 0080h | Bit
|  |  |  | 16367 | State external Digital Input 7 latched | Mask: 0040h | Bit
|  |  |  | 16366 | State external Digital Input 6 latched | Mask: 0020h | Bit
|  |  |  | 16365 | State external Digital Input 5 latched | Mask: 0010h | Bit
|  |  |  | 16364 | State external Digital Input 4 latched | Mask: 0008h | Bit
|  |  |  | 16362 | State external Digital Input 3 latched | Mask: 0004h | Bit
|  |  |  | 16361 | State external Digital Input 2 latched | Mask: 0002h | Bit
|  |  |  | 16360 | State external Digital Input 1 latched | Mask: 0001h | Bit
450092 | 450091 | 30 | 3,4,5,6 | 2568 | Gen. hours of operation | 0.01 | h | 0 | 0 |  | 0
450094 | 450093 | 31 | 1,2 | 10033 | Alarm flexible limit 16 latched | Mask: 8000h | Bit | 0 | 0 |  | 0
|  |  |  | 10032 | Alarm flexible limit 15 latched | Mask: 4000h | Bit
|  |  |  | 10031 | Alarm flexible limit 14 latched | Mask: 2000h | Bit
|  |  |  | 10030 | Alarm flexible limit 13 latched | Mask: 1000h | Bit
|  |  |  | 10029 | Alarm flexible limit 12 latched | Mask: 0800h | Bit
|  |  |  | 10028 | Alarm flexible limit 11 latched | Mask: 0400h | Bit
|  |  |  | 10027 | Alarm flexible limit 10 latched | Mask: 0200h | Bit
|  |  |  | 10026 | Alarm flexible limit 9 latched | Mask: 0100h | Bit
|  |  |  | 10025 | Alarm flexible limit 8 latched | Mask: 0080h | Bit
|  |  |  | 10024 | Alarm flexible limit 7 latched | Mask: 0040h | Bit
|  |  |  | 10023 | Alarm flexible limit 6 latched | Mask: 0020h | Bit
|  |  |  | 10022 | Alarm flexible limit 5 latched | Mask: 0010h | Bit
|  |  |  | 10021 | Alarm flexible limit 4 latched | Mask: 0008h | Bit
|  |  |  | 10020 | Alarm flexible limit 3 latched | Mask: 0004h | Bit
|  |  |  | 10019 | Alarm flexible limit 2 latched | Mask: 0002h | Bit
|  |  |  | 10018 | Alarm flexible limit 1 latched | Mask: 0001h | Bit
450095 | 450094 | 31 | 3,4 | 10117 | Analog input 4 | changeable |  | 31 | 54 |  | 79
450096 | 450095 | 31 | 5,6 |  | internal |  |  | 1 | 1 |  | 438
450097 | 450096 | 32 | 1,2 | 10008 | Batt.overvolt.2 latched | Mask: 0008h | Bit | 0 | 0 |  | 0
|  |  |  | 10007 | Batt.undervolt.2 latched | Mask: 0004h | Bit
|  |  |  | 10006 | Batt.overvolt.1 latched | Mask: 0002h | Bit
|  |  |  | 10005 | Batt.undervolt.1 latched | Mask: 0001h | Bit
450098 | 450097 | 32 | 3,4 |  | internal | Mask: 0001h | Bit | 0 | 0 |  | 0
|  |  |  | 10014 | Analog inp. 1, wire break or shortcut latched | Mask: 0002h | Bit
|  |  |  | 10015 | Analog inp. 2, wire break or shortcut latched | Mask: 0004h | Bit
|  |  |  | 10060 | Analog inp. 3, wire break or shortcut latched | Mask: 0008h | Bit
|  |  |  | 10061 | Analog inp. 4, wire break or shortcut latched | Mask: 0010h | Bit
[5 empty] | internal | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0040h | Bit
[5 empty] | internal | Mask: 0080h | Bit
[5 empty] | internal | Mask: 0100h | Bit
[5 empty] | internal | Mask: 0200h | Bit
[5 empty] | internal | Mask: 0400h | Bit
[5 empty] | internal | Mask: 0800h | Bit
[5 empty] | internal | Mask: 1000h | Bit
[5 empty] | internal | Mask: 2000h | Bit
[5 empty] | internal | Mask: 4000h | Bit
[5 empty] | internal | Mask: 8000h | Bit
450099 | 450098 | 32 | 5,6 | 10107 | Digital outputs 1 to 6 |  |  | 32768 | 32768 |  | 36865
[5 empty] | Relay-Output 1 (inverted) | Mask: 8000h | Bit
[5 empty] | Relay-Output 2 | Mask: 4000h | Bit
[5 empty] | Relay-Output 3 | Mask: 2000h | Bit
[5 empty] | Relay-Output 4 | Mask: 1000h | Bit
[5 empty] | Relay-Output 5 | Mask: 0800h | Bit
[5 empty] | Relay-Output 6 | Mask: 0400h | Bit
[5 empty] | internal | Mask: 0200h | Bit
[5 empty] | internal | Mask: 0100h | Bit
[5 empty] | internal | Mask: 0080h | Bit
[5 empty] | internal | Mask: 0040h | Bit
[5 empty] | internal | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0010h | Bit
[5 empty] | internal | Mask: 0008h | Bit
[5 empty] | internal | Mask: 0004h | Bit
[5 empty] | internal | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450100 | 450099 | 33 | 1,2 | 10109 | Digital outputs 7 to 11 |  |  | 256 | 256 |  | 8448
[5 empty] | Relay-Output 7 | Mask: 8000h | Bit
[5 empty] | Relay-Output 8 | Mask: 4000h | Bit
[5 empty] | Relay-Output 9 | Mask: 2000h | Bit
[5 empty] | Relay-Output 10 | Mask: 1000h | Bit
[5 empty] | Relay-Output 11 | Mask: 0800h | Bit
[5 empty] | internal | Mask: 0400h | Bit
[5 empty] | internal | Mask: 0200h | Bit
[5 empty] | internal | Mask: 0100h | Bit
[5 empty] | internal | Mask: 0080h | Bit
[5 empty] | internal | Mask: 0040h | Bit
[5 empty] | internal | Mask: 0020h | Bit
[5 empty] | internal | Mask: 0010h | Bit
[5 empty] | internal | Mask: 0008h | Bit
[5 empty] | internal | Mask: 0004h | Bit
[5 empty] | internal | Mask: 0002h | Bit
[5 empty] | internal | Mask: 0001h | Bit
450101 | 450100 | 33 | 3,4 | 8005 | Output to external CAN-I/O Relay 16 | Mask: 8000h | Bit | 0 | 0 |  | 0
[5 empty] | Output to external CAN-I/O Relay 15 | Mask: 4000h | Bit
[5 empty] | Output to external CAN-I/O Relay 14 | Mask: 2000h | Bit
[5 empty] | Output to external CAN-I/O Relay 13 | Mask: 1000h | Bit
[5 empty] | Output to external CAN-I/O Relay 12 | Mask: 0800h | Bit
[5 empty] | Output to external CAN-I/O Relay 11 | Mask:0400h | Bit
[5 empty] | Output to external CAN-I/O Relay 10 | Mask: 0200h | Bit
[5 empty] | Output to external CAN-I/O Relay 9 | Mask: 0100h | Bit
[5 empty] | Output to external CAN-I/O Relay 8 | Mask: 0080h | Bit
[5 empty] | Output to external CAN-I/O Relay 7 | Mask: 0040h | Bit
[5 empty] | Output to external CAN-I/O Relay 6 | Mask: 0020h | Bit
[5 empty] | Output to external CAN-I/O Relay 5 | Mask: 0010h | Bit
[5 empty] | Output to external CAN-I/O Relay 4 | Mask: 0008h | Bit
[5 empty] | Output to external CAN-I/O Relay 3 | Mask: 0004h | Bit
[5 empty] | Output to external CAN-I/O Relay 2 | Mask: 0002h | Bit
[5 empty] | Output to external CAN-I/O Relay 1 | Mask: 0001h | Bit
450102 | 450101 | 33 | 5,6 |  | internal |  |  | 0 | 0 |  | 0
450103 | 450102 | 34 | 1,2 | 5541 | Setpoint frequency | 0.01 | Hz | 5000 | 5000 |  | 5000
450104 | 450103 | 34 | 3,4,5,6 | 5542 | Setpoint active power | 0.1 | kW | 0 | 0 |  | 0
450106 | 450105 | 35 | 1,2 | 5641 | Setpoint power factor | 0.001 |  | 980 | 980 |  | 980
450107 | 450106 | 35 | 3,4,5,6 | 5640 | Setpoint voltage | 1 | V | 0 | 0 |  | 0
450109 | 450108 | 36 | 1,2 |  |  |  |  | 0 | 0 |  | 0
450110 | 450109 | 36 | 3,4 |  |  |  |  | 0 | 0 |  | 0
450111 | 450110 | 36 | 5,6 |  |  |  |  | 0 | 0 |  | 0
450112 | 450111 | 37 | 1,2 | 15109 | J1939 MTU ADEC ECU Failure Codes | 1 |  | 0 | 0 |  | 0
450113 | 450112 | 37 | 3,4 |  |  |  |  | 0 | 0 |  | 0
450114 | 450113 | 37 | 5,6 |  |  |  |  | 0 | 0 |  | 0
450115 | 450114 | 38 | 1,2 | 15304 | Engine Stop Information (extracted from DEUTZ- | 1 | (enu | 0 | 0 |  | 0
[5 empty] | specific J1939-Message) |  | m.)
450116 | 450115 | 38 | 3,4 |  |  |  |  | 0 | 0 |  | 0
450117 | 450116 | 38 | 5,6 |  |  |  |  | 0 | 0 |  | 0
450118 | 450117 | 39 | 1,2 | 15305 | J1939 DLN2-Message Scania S6 |  |  | 4369 | 4369 |  | 4369
Engine Coolant Temperature
[5 empty] | J1939-Message not available | Mask 8000h
[5 empty] | Sensor fault | Mask 4000h
[5 empty] | High Temperature. | Mask 2000h
[5 empty] | NOT High Temperature | Mask 1000h
Engine Oil Pressure
[5 empty] | J1939-Message not available | Mask 0800h
[5 empty] | Sensor fault | Mask 0400h
[5 empty] | Low Pressure | Mask 0200h
[5 empty] | NOT Low Pressure | Mask 0100h
High Engine Oil Level
[5 empty] | J1939-Message not available | Mask 0080h
[5 empty] | Sensor fault | Mask 0040h
[5 empty] | High Level | Mask 0020h
[5 empty] | NOT High Level | Mask 0010h
Low Engine Oil Level
[5 empty] | J1939-Message not available | Mask 0008h
[5 empty] | Sensor fault | Mask 0004h
[5 empty] | Low Level | Mask 0002h
[5 empty] | NOT Low Level | Mask 0001h
450119 | 450118 | 39 | 3,4 |  |  |  |  | 0 | 0 |  | 0
450120 | 450119 | 39 | 5,6 |  |  |  |  | 0 | 0 |  | 0
1. Active Diagnostic Trouble Code (DM1)
450121 | 450120 | 40 | 1 | 15401 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15402 | OC | Mask 00FFh
450122 | 450121 | 40 | 3,4,5,6 | 15400 | SPN |  |  | 0 | 0 |  | 0
2. Active Diagnostic Trouble Code (DM1)
450124 | 450123 | 41 | 1 | 15404 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15405 | OC | Mask 00FFh
450125 | 450124 | 41 | 3,4,5,6 | 15403 | SPN |  |  | 0 | 0 |  | 0
3. Active Diagnostic Trouble Code (DM1)
450127 | 450126 | 42 | 1 | 15407 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15408 | OC | Mask 00FFh
450128 | 450127 | 42 | 3,4,5,6 | 15406 | SPN |  |  | 0 | 0 |  | 0
4. Active Diagnostic Trouble Code (DM1)
450130 | 450129 | 43 | 1 | 15410 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15411 | OC | Mask 00FFh
450131 | 450130 | 43 | 3,4,5,6 | 15409 | SPN |  |  | 0 | 0 |  | 0
5. Active Diagnostic Trouble Code (DM1)
450133 | 450132 | 44 | 1 | 15413 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15414 | OC | Mask 00FFh
450134 | 450133 | 44 | 3,4,5,6 | 15412 | SPN |  |  | 0 | 0 |  | 0
6. Active Diagnostic Trouble Code (DM1)
450136 | 450135 | 45 | 1 | 15416 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15418 | OC | Mask 00FFh
450137 | 450136 | 45 | 3,4,5,6 | 15415 | SPN |  |  | 0 | 0 |  | 0
7. Active Diagnostic Trouble Code (DM1)
450139 | 450138 | 46 | 1 | 15420 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15421 | OC | Mask 00FFh
450140 | 450139 | 46 | 3,4,5,6 | 15419 | SPN |  |  | 0 | 0 |  | 0
8. Active Diagnostic Trouble Code (DM1)
450142 | 450141 | 47 | 1 | 15423 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15424 | OC | Mask 00FFh
450143 | 450142 | 47 | 3,4,5,6 | 15422 | SPN |  |  | 0 | 0 |  | 0
9. Active Diagnostic Trouble Code (DM1)
450145 | 450144 | 48 | 1 | 15426 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15427 | OC | Mask 00FFh
450146 | 450145 | 48 | 3,4,5,6 | 15425 | SPN |  |  | 0 | 0 |  | 0
10. Active Diagnostic Trouble Code (DM1)
450148 | 450147 | 49 | 1 | 15429 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15430 | OC | Mask 00FFh
450149 | 450148 | 49 | 3,4,5,6 | 15428 | SPN |  |  | 0 | 0 |  | 0
1. Previously Active Diagnostic Trouble Code
(DM2)
450151 | 450150 | 50 | 1 | 15451 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15452 | OC | Mask 00FFh
450152 | 450151 | 50 | 3,4,5,6 | 15450 | SPN |  |  | 0 | 0 |  | 0
2. Previously Active Diagnostic Trouble Code
(DM2)
450154 | 450153 | 51 | 1 | 15454 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15455 | OC | Mask 00FFh
450155 | 450154 | 51 | 3,4,5,6 | 15453 | SPN |  |  | 0 | 0 |  | 0
3. Previously Active Diagnostic Trouble Code
(DM2)
450157 | 450156 | 52 | 1 | 15457 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15458 | OC | Mask 00FFh
450158 | 450157 | 52 | 3,4,5,6 | 15456 | SPN |  |  | 0 | 0 |  | 0
4. Previously Active Diagnostic Trouble Code
(DM2)
450160 | 450159 | 53 | 1 | 15460 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15461 | OC | Mask 00FFh
450161 | 450160 | 53 | 3,4,5,6 | 15459 | SPN |  |  | 0 | 0 |  | 0
5. Previously Active Diagnostic Trouble Code
(DM2)
450163 | 450162 | 54 | 1 | 15463 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15464 | OC | Mask 00FFh
450164 | 450163 | 54 | 3,4,5,6 | 15462 | SPN |  |  | 0 | 0 |  | 0
6. Previously Active Diagnostic Trouble Code
(DM2)
450166 | 450165 | 55 | 1 | 15466 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15467 | OC | Mask 00FFh
450167 | 450166 | 55 | 3,4,5,6 | 15465 | SPN |  |  | 0 | 0 |  | 0
7. Previously Active Diagnostic Trouble Code
(DM2)
450169 | 450168 | 56 | 1 | 15469 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15470 | OC | Mask 00FFh
450170 | 450169 | 56 | 3,4,5,6 | 15468 | SPN |  |  | 0 | 0 |  | 0
8. Previously Active Diagnostic Trouble Code
(DM2)
450172 | 450171 | 57 | 1 | 15472 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15473 | OC | Mask 00FFh
450173 | 450172 | 57 | 3,4,5,6 | 15471 | SPN |  |  | 0 | 0 |  | 0
9. Previously Active Diagnostic Trouble Code
(DM2)
450175 | 450174 | 58 | 1 | 15475 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15476 | OC | Mask 00FFh
450176 | 450175 | 58 | 3,4,5,6 | 15474 | SPN |  |  | 0 | 0 |  | 0
10. Previously Active Diagnostic Trouble Code
(DM2)
450178 | 450177 | 59 | 1 | 15478 | FMI | Mask FF00h |  | 0 | 0 |  | 0
|  |  | 2 | 15479 | OC | Mask 00FFh
450179 | 450178 | 59 | 3,4,5,6 | 15477 | SPN |  |  | 0 | 0 |  | 0
450181 | 450180 | 60 | 1,2 | 15395 | DM1 Lamp Status |  |  | 4369 | 4369 |  | 4369
Malfunction Lamp
[5 empty] | internal | Mask 8000h
[5 empty] | internal | Mask 4000h
[5 empty] | On | Mask 2000h
[5 empty] | Off | Mask 1000h
Red Stop Lamp
[5 empty] | internal | Mask 0800h
[5 empty] | internal | Mask 0400h
[5 empty] | On | Mask 0200h
[5 empty] | Off | Mask 0100h
Amber Warning Lamp
[5 empty] | internal | Mask 0080h
[5 empty] | internal | Mask 0040h
[5 empty] | On | Mask 0020h
[5 empty] | Off | Mask 0010h
Protect Lamp
[5 empty] | internal | Mask 0008h
[5 empty] | internal | Mask 0004h
[5 empty] | On | Mask 0002h
[5 empty] | Off | Mask 0001h
450182 | 450181 | 60 | 3,4 | 15445 | DM2 Lamp Status |  |  | 4369 | 4369 |  | 4369
Malfunction Lamp
[5 empty] | internal | Mask 8000h
[5 empty] | internal | Mask 4000h
[5 empty] | On | Mask 2000h
[5 empty] | Off | Mask 1000h
Red Stop Lamp
[5 empty] | internal | Mask 0800h
[5 empty] | internal | Mask 0400h
[5 empty] | On | Mask 0200h
[5 empty] | Off | Mask 0100h
Amber Warning Lamp
[5 empty] | internal | Mask 0080h
[5 empty] | internal | Mask 0040h
[5 empty] | On | Mask 0020h
[5 empty] | Off | Mask 0010h
Protect Lamp
[5 empty] | internal | Mask 0008h
[5 empty] | internal | Mask 0004h
[5 empty] | On | Mask 0002h
[5 empty] | Off | Mask 0001h
450183 | 450182 | 60 | 5,6 |  | internal |  |  | 0 | 0 |  | 0
450184 | 450183 | 61 | 1,2 | 15308 | Engine Speed (j1939-EEC1) | 1 | rpm | 32767 | 32767 |  | 32767
450185 | 450184 | 61 | 3,4 | 15202 | Engine Coolant Temperature (J1939-ET1) | 1 | °C | 32767 | 32767 |  | 32767
450186 | 450185 | 61 | 5,6 | 15205 | Engine Oil Pressure (j1939-EFL/P1) | 1 | kPa | 32767 | 32767 |  | 32767
450187 | 450186 | 62 | 1,2 | 15203 | Fuel temperature (j1939-ET1) | 1 | °C | 32767 | 32767 |  | 32767
450188 | 450187 | 62 | 3,4,5,6 | 15201 | Total engine hours (j1939-HOURS) | 1 | h | 65535 | 65535 |  | 65536
450190 | 450189 | 63 | 1,2 | 15309 | Engine Oil Temperature (j1939-ET1) | 0.1 | °C | 32767 | 32767 |  | 32767
450191 | 450190 | 63 | 3,4 | 15307 | Fuel Rate (j1939-LFE) | 0.1 | L/h | 32767 | 32767 |  | 32767
450192 | 450191 | 63 | 5,6 | 15206 | Coolant Level (j1939-EFL/P1) | 0.1 | % | 32767 | 32767 |  | 32767
450193 | 450192 | 64 | 1,2 | 15207 | Throttle position (j1939-EEC2) | 0.1 | % | 32767 | 32767 |  | 32767
450194 | 450193 | 64 | 3,4 | 15208 | Load at current Speed (j1939-EEC2) | 1 | % | 32767 | 32767 |  | 32767
450195 | 450194 | 64 | 5,6 | 15210 | Engine oil level (j1939-EFL/P1) | 0.1 | % | 32767 | 32767 |  | 32767
450196 | 450195 | 65 | 1,2 | 15214 | Boost pressure (j1939-IC1) | 1 | kPa | 32767 | 32767 |  | 32767
450197 | 450196 | 65 | 3,4 | 15215 | Intake Manifold Temp (j1939-IC1) | 1 | °C | 32767 | 32767 |  | 32767
450198 | 450197 | 65 | 5,6 | 15212 | Barometric Pressure (j1939-AMB) | 0.1 | kPa | 32767 | 32767 |  | 32767
450199 | 450198 | 66 | 1,2 | 15213 | Air inlet temperature (j1939-AMB) | 1 | °C | 32767 | 32767 |  | 32767
450200 | 450199 | 66 | 3,4 | 15209 | Actual engine torque (j1939-EEC1) | 1 | % | 32767 | 32767 |  | 32767
450201 | 450200 | 66 | 5,6 | 15299 | Exhaust Gas Temp.(J1939-IC1) | 0.1 | °C | 32767 | 32767 |  | 32767

## Modbus All Values
Register | Inactive Value 1 | Inactive Value 2 | Active Value 1 | Active Value 2 | All Values from 50001 - 50201
450001 | 5100 |  |  | 5100
450002 | 0 |  |  | 1500
450003 | 3601 |  |  | 3601
450004 | 1000 |  |  | 974
450005 | 0 |  |  | 0
450006 | 0 |  |  | 2306
450007 | 0 |  |  | 5001
450008 | 0 |  |  | 0
450009 | 0 |  |  | 3996
450010 | 5002 |  |  | 5001
450011 | 0 |  |  | 0
450012 | 2309 |  |  | 2306
450013 | 1000 |  |  | 1000
450014 | 0 |  |  | 0
450015 | 4000 |  |  | 3995
450016 | 116 |  |  | 79
450017 | 0 |  |  | 2
450018 | 0 |  |  | 58834
450019 | 13253 |  |  | 13251
450020 | 0 |  |  | 0
450021 | 0 |  |  | 0
450022 | 270 |  |  | 281
450023 | 0 |  |  | 0
450024 | 0 |  |  | 0
450025 | 32767 |  |  | 23767
450026 | 0 |  |  | 4
450027 | 0 |  |  | 19856
450028 | 32767 |  |  | 32767
450029 | 0 |  |  | 0
450030 | 0 |  |  | 0
450031 | 32767 |  |  | 32767
450032 | 0 |  |  | 0
450033 | 0 |  |  | 25500
450034 | 1024 |  |  | 2536
450035 | 0 |  |  | 4
450036 | 0 |  |  | 31856
450037 | 4096 |  |  | 20480
450038 | 0 |  |  | 4
450039 | 0 |  |  | 365
450040 | 0 |  |  | 2048
450041 | 0 |  |  | 4
450042 | 0 |  |  | 27356
450043 | 0 |  |  | 900
450044 | 0 |  |  | 0
450045 | 0 |  |  | 0
450046 | 64 |  |  | 64
450047 | 0 |  |  | 0
450048 | 0 |  |  | 38971
450049 | 4340 |  |  | 5053
450050 | 0 |  |  | 0
450051 | 0 |  |  | 0
450052 | 4999 |  |  | 4884
450053 | 0 |  |  | 0
450054 | 0 |  |  | 3999
450055 | 0 |  |  | 9993
450056 | 0 |  |  | 0
450057 | 0 |  |  | 2303
450058 | 0 |  |  | 9993
450059 | 0 |  |  | 0
450060 | 0 |  |  | 4002
450061 | 0 |  |  | 284
450062 | 0 |  |  | 0
450063 | 0 |  |  | 2308
450064 | 0 |  |  | 0
450065 | 0 |  |  | 0
450066 | 0 |  |  | 3998
450067 | 0 |  |  | 0
450068 | 0 |  |  | 0
450069 | 0 |  |  | 2318
450070 | 293 |  |  | 297
450071 | 0 |  |  | 0
450072 | 3993 |  |  | 4002
450073 | 0 |  |  | 0
450074 | 0 |  |  | 0
450075 | 2304 |  |  | 2306
450076 | 0 |  |  | 0
450077 | 0 |  |  | 0
450078 | 4001 |  |  | 4009
450079 | 0 |  |  | 0
450080 | 0 |  |  | 0
450081 | 2308 |  |  | 2312
450082 | 0 |  |  | 0
450083 | 0 |  |  | 0
450084 | 3999 |  |  | 4004
450085 | 512 |  |  | 512
450086 | 0 |  |  | 0
450087 | 2311 |  |  | 2318
450088 | 0 |  |  | 0
450089 | 0 |  |  | 0
450090 | 984 |  |  | 105
450091 | 0 |  |  | 0
450092 | 0 |  |  | 0
450093 | 2608 |  |  | 908
450094 | 0 |  |  | 0
450095 | 47 |  |  | 82
450096 | 3 |  |  | 434
450097 | 0 |  |  | 0
450098 | 0 |  |  | 0
450099 | 32769 |  |  | 36865
450100 | 256 |  |  | 8448
450101 | 0 |  |  | 0
450102 | 0 |  |  | 0
450103 | 5000 |  |  | 5000
450104 | 0 |  |  | 0
450105 | 0 |  |  | 0
450106 | 980 |  |  | 980
450107 | 0 |  |  | 0
450108 | 400 |  |  | 400
450109 | 0 |  |  | 0
450110 | 0 |  |  | 0
450111 | 0 |  |  | 0
450112 | 0 |  |  | 0
450113 | 0 |  |  | 0
450114 | 0 |  |  | 0
450115 | 0 |  |  | 0
450116 | 0 |  |  | 0
450117 | 0 |  |  | 0
450118 | 4369 |  |  | 4369
450119 | 0 |  |  | 0
450120 | 0 |  |  | 0
450121 | 0 |  |  | 0
450122 | 0 |  |  | 0
450123 | 0 |  |  | 0
450124 | 0 |  |  | 0
450125 | 0 |  |  | 0
450126 | 0 |  |  | 0
450127 | 0 |  |  | 0
450128 | 0 |  |  | 0
450129 | 0 |  |  | 0
450130 | 0 |  |  | 0
450131 | 0 |  |  | 0
450132 | 0 |  |  | 0
450133 | 0 |  |  | 0
450134 | 0 |  |  | 0
450135 | 0 |  |  | 0
450136 | 0 |  |  | 0
450137 | 0 |  |  | 0
450138 | 0 |  |  | 0
450139 | 0 |  |  | 0
450140 | 0 |  |  | 0
450141 | 0 |  |  | 0
450142 | 0 |  |  | 0
450143 | 0 |  |  | 0
450144 | 0 |  |  | 0
450145 | 0 |  |  | 0
450146 | 0 |  |  | 0
450147 | 0 |  |  | 0
450148 | 0 |  |  | 0
450149 | 0 |  |  | 0
450150 | 0 |  |  | 0
450151 | 0 |  |  | 0
450152 | 0 |  |  | 0
450153 | 0 |  |  | 0
450154 | 0 |  |  | 0
450155 | 0 |  |  | 0
450156 | 0 |  |  | 0
450157 | 0 |  |  | 0
450158 | 0 |  |  | 0
450159 | 0 |  |  | 0
450160 | 0 |  |  | 0
450161 | 0 |  |  | 0
450162 | 0 |  |  | 0
450163 | 0 |  |  | 0
450164 | 0 |  |  | 0
450165 | 0 |  |  | 0
450166 | 0 |  |  | 0
450167 | 0 |  |  | 0
450168 | 0 |  |  | 0
450169 | 0 |  |  | 0
450170 | 0 |  |  | 0
450171 | 0 |  |  | 0
450172 | 0 |  |  | 0
450173 | 0 |  |  | 0
450174 | 0 |  |  | 0
450175 | 0 |  |  | 0
450176 | 0 |  |  | 0
450177 | 0 |  |  | 0
450178 | 0 |  |  | 0
450179 | 0 |  |  | 0
450180 | 0 |  |  | 0
450181 | 4369 |  |  | 4369
450182 | 4369 |  |  | 4369
450183 | 0 |  |  | 0
450184 | 32767 |  |  | 32767
450185 | 32767 |  |  | 32767
450186 | 32767 |  |  | 32767
450187 | 32767 |  |  | 32767
450188 | 65535 |  |  | 65535
450189 | 65535 |  |  | 65535
450190 | 32767 |  |  | 32767
450191 | 32767 |  |  | 32767
450192 | 32767 |  |  | 32767
450193 | 32767 |  |  | 32767
450194 | 32767 |  |  | 32767
450195 | 32767 |  |  | 32767
450196 | 32767 |  |  | 32767
450197 | 32767 |  |  | 32767
450198 | 32767 |  |  | 32767
450199 | 32767 |  |  | 32767
450200 | 32767 |  |  | 32767
450201 | 32767 |  |  | 32767